## Instructions
OTCR2 Application Instructions
As a part of the OTCR2 application process, applicants must provide specific information and documentation outlined within this checklist. This checklist document is split into three tabs, "Project Info", "Certs, Reports", and "Plans (Project Guidelines)". Guidance on how to use this checklist appropriately is found below. Additionally, a Required Documents Checklist is available below for use as a reference to understand and collate all requested documentation. When submitting the documents for review, please indicate in the file name which tab/letter they apply to. For example, “2a_UL 9540 certificate”. The "Project Info" tab contains general information that OTCR requires as a part of the approval process. Please type in the appropriate information in the "Applicant Responses" column, Column D. OTCR will then review and date when approved. The "Certs, Reports" tab requires specified documentation for OTCR review and approval. Please see the Required Documents Checklist or review the tab to understand which documents are required for review. OTCR will review and either provide objections/comments and request a resubmittal or indicate the document has been approved. You are not required to fill anything out in this tab. The "Plans" tab contains specific plan sheets that are required for OTCR review and approval. These include the Battery Plan, Fire Protection Plan, and Zoning Plan sets. Each page of the plan set must be signed and sealed. Specific guidelines for what each plan sheet needs to include are outlined within the tab. This tab also contains requirements for flood zone analysis and the commissioning plan. OTCR will review the provided documents and either provide objections/comments and request a resubmittal or indicate that the document has been approved. You are not required to fill anything out in this tab. Should any questions or concerns come up throughout the process, please contact your assigned application reviewer.
Required Documents Checklist
| Document Name | OTCR Requirement Reference | ü
| UL 9540 Certificate | 2a
| UL 9540A Test Report (cell) | 2b
| UL 9540A Test Report (module) | 2b
| UL 9540A Test Report (unit) | 2b
| FDNY Certificate Of Approval (COA) | 2c
| FDNY Letter of Conditional Acceptance (LCA) as required per the FDNY code and rule | 2d
| Battery Plan Set | 3a
| Commissioning Plan | 3b

## 1 - Project Info
# | Requirement | Description | Applicant Responses
1a | Address of the Installation | Address
1b | Product information of the Energy Storage System (ESS) | ESS manufacturer name, product name, and model number
1c | Contact information of the Registered Design Professional of record (RDP) | RDP's name, company, address, telephone #, and email
1d | Contact information of the Integrator | Integrator's name, company, address, telephone #, and email
1e | Contact information of the Owner | Owner's name, company, address, telephone #, and email
1f | DOB Job # | A DOB Now application must be filed for the proposed ESS, and a job # will be issued upon filing.

## 2 - ESS Properties (hidden)
# | Requirement | Description | DNV Review Status | Objective / Purpose / Scope of review | OTCR / Code Requirement | Submission required by: RDP, Manufact., N/A | Applicant Responses (Include document name, if applicable) | File Name (Word doc or pdf) | Relevant Document / Sheet | Details | DNV Notes | Conclusion | Acceptable (Y/N) | OTCR Objections | OTCR Acceptance Date
2a | ESS and Inverter Info | ESS Chemistry (i.e., Lithium-Ion, etc.) |  | This information is required while drafting the conditional acceptance letter. | N/A | Open
|  | Battery Model, Make and Series (as referenced in listing and testing documents) |  | This information is required while drafting the conditional acceptance letter. | This Battery model has to be matched with the UL 9540 certification and UL 9540A testing report.
|  | Number of Batteries (total batteries proposed for project) |  | This information is required while drafting the conditional acceptance letter. | N/A
|  | Battery Capacity (kWh / MWh total for project) |  | This information is required while drafting the conditional acceptance letter. | N/A
2b | Published literature | Battery |  | Information collecting | N/A | Open
|  | Inverter |  | Information collecting | N/A
|  | BMS |  | Information collecting | N/A

## 3 - Hazards (hidden)
# | Requirement | Description | DNV Review Status | Objective / Purpose / Scope of review | OTCR / Code Requirement | Submission required by: RDP, Manufact., N/A | Applicant Responses (Include document name, if applicable) | File Name (Word doc or pdf) | Relevant Document / Sheet | Details | DNV Notes | Conclusion | Acceptable (Y/N) | OTCR Objections | OTCR Acceptance Date
3a | Identify hazards | RDP must state if project requires compliance with BC 414.1.3. If so, please submit a copy of the RDP (signed and sealed) report required by BC 414.1.3. Note: This is for indoor installations only. |  | Identification of hazardous materials on site. | BC Section 414.1.3 | RDP (Note: Not necessary to be signed and sealed.)

## 2 - Certs, Reports
# | Requirement | Description | OTCR Objections | Comments | OTCR Acceptance Date
2a | ESS Listing | UL 9540 listing certificate. For applications submitted prior to 4/15/2022, UL 9540 1st or 2nd ed. is acceptable. For applications submitted after 4/15/2022, ESS must be certified to UL 9540 2nd ed.
2b | ESS Full Scale Testing | UL 9540A (4th ed.) test report; including all applicable levels (cell, module, unit, and installation levels).
2c | FDNY Certificate Of Approval (COA) | Equipment approval is required per the Fire Code.
2d | FDNY Letter of Conditional Acceptance (LCA) | Installation approval as required per the FDNY code and rule.

## 3 - Plans (Project Guidelines)
# | Requirement | Description | OTCR Objections (As applicable) | Comments | Date Resolved
3a | Battery Plan Set (see sample plans for reference) | Show location and layout of the room / area where the proposed ESS will be installed, and provide details of all nearby exposures in the drawings (e.g., uses and occupancy group of the nearby buildings).
Show distances between the ESS and the following exposures: 1. Lot lines; 2. Public streets, fire apparatus access road, public walkways and other public ways; 3. Any vehicle parking; 4. Any building/structure with indications of entrances, doors, openable windows, access hatches, or ventilation intakes; 5. Any egress features from a building or outdoor area; 6. Any hazardous materials or combustible materials storage facility or area; 7. Any storage facility or area for high-piled combustible materials or other combustible items; 8. Overhead power lines or other aboveground electrical installation, measured from the boundary of the utility easement or, if there is no easement, from the vertical plane of the installation at its widest point; 9. Any public utility or transportation infrastructure; 10. Any equipment;
Security features and impact protections (e.g., fencing, bollards, etc.).
Manufacturer specifications, including pictures and dimensions of the ESS.
Provide a general note box with the following information: 1. ESS chemistry (i.e., lithium-ion (LFP, NMC, etc.)) 2. Battery model, make and series (as referenced in listing and testing documents). 3. Number of batteries (total batteries proposed for project). 4. Battery capacity (total kWh for the project). 5. Inverter model, make, and series (as referenced in listing and testing documents). 6. Installation location (indoor, outdoor, or rooftop) 7. Energy Source (e.g., solar, grid, CHP, etc.). 8. Energy Output (e.g., grid, building(s) within the zoning lot, etc.). 9. If free electrolyte provide: (1) total electrolyte (2) volume, container volume, (3) secondary containment volume.
The following certification statement for code compliance, signed and sealed by the RDP, shall be provided on the Battery Plan Set: "I __________, the Registered Design Professional of record, certify that, to the best of my knowledge, belief and professional judgment, the proposed energy storage system complies with all applicable requirements under the New York City Construction Codes, the New York City Electrical Code, the New York City Fire Code, and all other pertinent laws, rules, and regulations. I understand falsification of any statement is a misdemeanor and is punishable by a fine or imprisonment. I understand that if I am found after hearing to have knowingly or negligently made a false statement or to have knowingly or negligently falsified or allowed to be falsified any certificate, form, signed statement, application, report or certification of the correction of a violation required under the provisions of this code or of a rule of any agency, I may be barred from filing further applications or documents with the Department."
The following certification statement for the proposed ESS project is designed to account for the UL 9540A test resuslts, signed and sealed by the RDP, shall be provided on the Battery Plan Set: "I __________, the Registered Design Professional of record, certify that, to the best of my knowledge, belief and professional judgment, the proposed energy storage system project is designed to account for the UL 9540A test results. I understand falsification of any statement is a misdemeanor and is punishable by a fine or imprisonment. I understand that if I am found after hearing to have knowingly or negligently made a false statement or to have knowingly or negligently falsified or allowed to be falsified any certificate, form, signed statement, application, report or certification of the correction of a violation required under the provisions of this code or of a rule of any agency, I may be barred from filing further applications or documents with the Department."
For indoor installations: Provide fire rating of the room containing the ESS.
For rooftop installations: Provide description of roofing material, including but not limited to, non-combustible or combustible construction, roof assembly classification, fire rating, etc.
Show locations and contents of all required signages, including but not limited to the following (see attached sample plan for reference): (A) Posted near the entrance gate: 1. OEM 24/7 contact number. 2. Installing contractor's contact number. 3. System rated kW, kWh, and voltages. 4. Battery chemistry. 5. Site plan showing egress and EPO locations. (B) Posted on each container: 1. Site plan showing egress and EPO locations. 2. Rated kWh for container. 3. NFPA 704 hazard identification diamond. 4. NFPA 70E label providing arc flash hazard information. (C) Posted on switchgear: 1. NFPA 70E label providing arc flash hazard information. 2. Label indicating main disconnect. (D) Warning, identification, emergency contact, and emergency shut-down signs as required by the FDNY.
Details on ventilation, exhaust, and deflagration venting systems for flammable gas.
DOB and/or FDNY application numbers of all relative fire protection systems filings, including but not limited to fire alarm and sprinkler systems.
Show dunnage / structural support.
The following certification statement for noise control regulation compliance, signed and sealed by the RDP, shall be provided on the Battery Plan Set: "I __________, the Registered Design Professional of record, certify that, to the best of my knowledge, belief and professional judgment, the proposed energy storage system has been evaluated using standard acoustical engineering methods and vendor provided source sound data. To the best of our knowledge, belief and professional judgment, this project if constructed in accordance with the design documents and with the recommendations given in our report will comply with Section 313 of the New York City Mechanical Code, and the New York City Noise Control Code. I understand falsification of any statement is a misdemeanor and is punishable by a fine or imprisonment. I understand that if I am found after hearing to have knowingly or negligently made a false statement or to have knowingly or negligently falsified or allowed to be falsified any certificate, form, signed statement, application, report or certification of the correction of a violation required under the provisions of this code or of a rule of any agency, I may be barred from filing further applications or documents with the Department."
3b | Commissioning Plan | Provide commissioning plan as required.

## Additional DNV Comments (hidden)
Additional DNV Comments
Are we still going to require BMS monitoring services? Or will this now be an item in the CAL? | A letter from the applicant stating that (ex. Tesla monitoring system)the required parameters will be monitored, is good enough for CAL.
I'd recommend still requiring an ERP | I agree with this statement; wondered why it was removed (PAF) | Site specific ERP, emergency shut down procedure shall be included for CAL.
I'd recommend still requiring a decommissioning plan
I'd recommend instructions page for applicant (i.e. when requesting page number from plan or document); this is often not given; makes it easier to identify (PAF)
Are Incident Training Manuals / Maintenance Plans / Recycling Plan no longer required? (MZ)
I'd recommend including a list of required documents somewhere in this document as well. (CK)
Note on A2: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Possibly covered in the FDNY review process. To confirm. Reply: FDNY looks at this
Note on A3: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: FDNY looks at this
Note on A4: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Apart of the COA
Note on A6: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: FDNY already looking at this

## 5 - Proposed Design Features (hidden)
See Tab 4 - Plans

## 7 - 24 hr BMS Monitoring (hidden)
# | Requirement | Description | DNV Review Status | Objective / Purpose / Scope of review | OTCR / Code Requirement | Submission required by: RDP, Manufact., N/A | Applicant Responses (Include document name, if applicable) | File Name (Word doc or pdf) | Relevant Document / Sheet | Details | DNV Notes | Conclusion | Acceptable (Y/N) | OTCR Objections | OTCR Acceptance Date
7a | Contract | Signed contract with owner and service provider. |  | Ensure that proper monitoring of ESS will be in place. | If site owner is not operating the ESS then applicant needs to provide a contract between the operator and the entity that is monitoring BMS activity. | Open
7b | Monitoring Parameters | i.e. voltage, current, temperature. |  | Ensure that proper monitoring of ESS will be in place. | Confirmation that voltage, current and temperature are monitored. Contract to state that faults are monitored and reported back to the monitoring center. | Open

## 8 - Manuals (hidden)
# | Requirement | Description | DNV Review Status | Objective / Purpose / Scope of review | OTCR / Code Requirement | Submission required by: RDP, Manufact., N/A | Applicant Responses (Include document name, if applicable) | File Name (Word doc or pdf) | Relevant Document / Sheet | Details | DNV Notes | Conclusion | Acceptable (Y/N) | OTCR Objections | OTCR Acceptance Date
8a | Incident Training Manual | MSDS, SDS (include page #) |  | Emergency preparedness | N/A | Open
|  | Employee hazardous material training document (include page #) |  | Emergency preparedness | N/A
|  | Emergency shutdown procedures (include page #) |  | Emergency preparedness | N/A
|  | Emergency first-aid requirements (include page #) |  | Emergency preparedness | N/A
|  | Emergency response plan (include page #) |  | Emergency preparedness | N/A
|  | Operation and training program manual (include page #) |  | Emergency preparedness | N/A
|  | Safety and handling guidelines (include page #) |  | Emergency preparedness | N/A
8b | Maintenance Plan | Details for replacement |  | Maintenance details of ESS | N/A | Open
|  | Compatibility of replacement parts |  | Maintenance details of ESS | N/A
8c | Recycling Plan | Recycling details, Decommissioning plan |  | End of life management | NFPA 855, Chapter 8 | Open

## 4 - Additional Reqs (hidden)
# | Requirement | Description | DNV Review Status | Objective / Purpose / Scope of review | OTCR / Code Requirement | Submission required by: RDP, Manufact., N/A | Applicant Responses (Include document name, if applicable) | File Name (Word doc or pdf) | Relevant Document / Sheet | Details | DNV Notes | Conclusion | Acceptable (Y/N) | OTCR Objections | OTCR Acceptance Date
9b | Code Analysis | Complete “Attachment A” |  | Code compliance | Provide completed word version of code analysis document, before the documents is signed and sealed by PE. OTCR will provide comments on the word version. | RDP, Signed and Sealed Letter
| MC 502.4 and 502.5 (Exhaust Requirements) | MC 502.4 - Stationary storage battery systems |  | Code compliance | MC 502.4 and 502.5
MC 502.4.1 - Hydrogen limiting rooms
MC 502.4.2 - Ventilation rate in rooms
MC 502.5 - Valve-regulated lead-acid batteries in cabinets
MC 502.5.1 - Hydrogen limit in cabinets
MC 502.5.2 - Ventilation rate in cabinets
| BC 509 (Separation of Incidental Use Areas) | BC 509.1 - General |  | Code compliance | BC 509
BC 509.2 - Occupancy Classification
BC 509.4 - Separation and protection
BC 509.4.1 - Separation
BC Table 509 - Incidental Uses
| BC 907.2 (Automatic Smoke Detection Requirements) | BC 907.2.21 - Battery rooms |  | Code compliance | BC 907
| FC 608 (Stationary Storage Battery Systems) | FC 608.2.2 - Recombinant batteries |  | Code compliance | FC 608
FC 608.3 - Thermal runaway
FC 608.4 - Room design and construction
FC 608.5 - Spill control and neutralization
FC 608.5.2 - Recombinant battery
FC 608.6 - Ventilation
FC 608.6.1 - Room ventilation
FC 608.7 - Signage
FC 608.7.1 - Equipment room and building signage
FC 608.7.2 - Cabinet signage
FC 608.8 - Seismic protection
FC 608.9 - Smoke detection
FC 608.10 - Emergency procedures
| BC 307 – (HIGH-HAZARD GROUP H) | BC 307.1 - High-hazard Group H |  | Code compliance | BC 307 & BC 414.1.3
BC 414.1.3 - Required information
| Structural Requirements (Ie, Dunnage & Concrete Pad) | BC 16 & BC 22 - Steel |  | Code compliance | BC 16, BC 22 and BC 19
BC 16 & BC 19 - Concrete
| Electrical Code | NYC EC 2011 |  | Code compliance | NYC EC 2011
|  | RCNY 4000-01(a) |  |  | RCNY 4000-01(a)
4c | DOB Required Item | After filing your ESS construction documents under “full plan review”, contact your assigned plan examiner(s) and request the addition of the required item in the BIS virtual folder called “OTCR Final Acceptance Letter”. DO NOT add the required item to related job filings for the ESS, such as fire alarms |  |  | To be completed by the applicant. Final acceptance will not be issued until this item is complete. Not applicable if application was filed through DOB NOW. | RDP, Manufacturer or the expediter | We will train the HUB for adding the required document into DOB NOW