## Inverts
2 -Invert Elevations, Slopes, & Velocities for House/Site Connections & Instructions -03/02/15
Sewer in:
Between: | [6 empty] | and:
BRONX |  | BROOKLYN |  |  | MANHATTAN |  |  | QUEENS |  |  |  | STATEN ISLAND
Swr.Dtm. | NAVD88 | Hwy.Dtm. | Swr.Dtm. | NAVD88 | Swr.Dtm. |  | NAVD88 | Swr.Dtm. |  | NAVD88 |  | Swr.Dtm. | NAVD88
| 1.508 | -0.84 |  | 0.607 |  |  | 1.652 |  |  | 1.625 |  |  | 2.092
Upstm.Mh.Rim |  |  | Upstm.Mh.Inv. |  |  | Dwnstm.Mh.Rim. |  |  | Dwnstm.Mh.Inv. |  |  | Mh.Dst.-ft.
Dn.St.Mh.-Cn.(ft.) |  |  | Dst.P.L.-Swr.(ft.) |  |  | Cir.Swr.Dia./Ht.-in. |  |  | Bx.Swr.Hgt.-ft. |  |  | Inv.Cn.@ P.L.
Dia.Cn.Swr.-in. |  |  | El.St.@Cn. |  | #DIV/0! |  | Rsr.-ft. |  |  | Dia.Cn.Mh..-in.
Inv.El.Swr.@Cn. |  | #DIV/0! |  | Comp.El.St.@Cn. |  | #DIV/0! | Swr.Cvr.@Cn.-ft. |  |  | #DIV/0! | Min.Rsr.Lgth.-(ft.) |  | #DIV/0!
Min.Inv.Cn.@Cir.Swr. |  |  | 0 | Max.Inv.Cn.@Cir.Swr. |  |  | 0 | Inv.Cn.@Bx.Swr. |  |  | 0 | Inv.Cn.@Rsr. | 0
Max.%Slp.Cn.@Cir.Swr. |  |  | 0 | Min.%Slp.Cn.@Cir.Swr. |  |  | 0 | %Slp.Cn.@Bx.Swr. |  |  | 0 | %Slp.Cn.@Rsr. | 0
|  |  | Dia.Cn. | Cir @ 75% |  | Cir @ 92% |  |  | Box |  |  | Riser
Connection Pipe Material |  |  | (in.) | cfs | fps | cfs | fps |  | cfs | fps |  | cfs | fps
Ductile Iron - 6 to 48 inch |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0
ESVP & EHCI - 6 to 22 in. |  |  | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 |  | 0 | 0
RCP - 24 to 72 inch | [8 empty] | 0 | 0
MANHOLE CONNECTION
[7 empty] | DUCTILE IRON |  |  | ESVP & EHCI |  | RCP
[7 empty] | (cfs) | (fps) |  | (cfs) | (fps) | (cfs) | (fps)
Min.Inv.Cir.Swr. |  | 0 | Max.%Slp.Cir.Swr. |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
Max.Inv.Cir.Swr. |  | 0 | Min.%Slp.Cir.Swr. |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
Min.Inv.Bx.Swr. |  | 0 | Max.%Slp.Bx.Swr. |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
Max.Inv.Bx.Swr. |  | 0 | Min.%Slp.Bx.Swr. |  | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0
Instructions
FEMA has issued a directive for conversion from borough highway datum to NAVD88 datum throught the city based on information from NOAA. If elevations on the
site plan are in NAVD88 datum, enter sewer datum elevation under the boro and NAVD88 elevation is to the right, and for Brooklyn Highway datum is to the left. For
each proposed conn. next to the appropriate cell enter: upstream & downstream manhole rin & invert elevations in appropriate datum, of sewer connecting to; distance
in ft. between manholes next to Mh.Dst.-ft.; distance in ft. from downstream manhole to conn. next to Dn.St.Mh.-Cn.(ft.); distance in ft. from property line or building
line to sewer connecting to next to Dst.P.L.-Swr.(ft.); diameter or height in inches of sewer if connecting to a circular/brick egg sewer next to Cir.Swr.Dia./Ht.-in., or
height in ft. if connecting to a box/flat top circular bottom reinforced concrete section sewer next to Bx.Swr.Hgt.-ft.; invert of conn. at property line in appropriate
datum next to Inv.Cn.@P.L.; diameter of conn. in inches if connecting directly to sewer next to Dia.Cn.Swr.-in.; elevation of street at conn. in appropriate datum if
known next to El.St.@Cn., and if the elevation is not known insert the value shown next to Comp.El.St.@Cn.; length in ft. of a standard riser if proposed, (cannot be
less than 3 ft.), next to Rsr.-ft.
Invert elevation of sewer at conn. is next to Inv.El.Swr.@Cn. If cover on sewer at connection, shown next to Swr.Cvr.@Cn.-ft., is 13 ft. or more a riser is required.
Minimum length in ft. of a riser if required is next to Min.Rsr.Lgth.-(ft.). If ground water or rock is present, or if there is interference from utilities riser may be built to
a higher elevation as required (maximum length 15 ft.). Riser on a box/flat top circular bottom reinforced concrete section sewer, or larger than 8 inches in diameter
requires approval from the Plan Review Section, as these are non-standard. A conn. with less than 4 ft. of cover must be encased in 6 inches of concrete.
Minimum invert elevation of conn. to circular/brick egg sewer is next to Min.Inv.Cn.@Cir.Swr., and maximum invert elevation is next to Max.Inv.Cn.@Cir.Swr..
Invert elevation of conn. to a box/flat top circular bottom reinforced concrete section sewer is next to Inv.Cn.@Bx.Swr.. Invert elevation of conn to a standard riser is
next to Inv.Cn.@Rsr.. Maximum slope as a % for conn. to a circular or brick egg sewer without a riser is next to Max.%Slp.Cn.@Cir.Swr., and minimum slope as a
% is next to Min.%Slp.Cn.@Cir.Swr.. Slope as a % for conn. to a box/flat top circular bottom reinforced concrete section sewer is next to %Slp.Cn.@Bx.Swr..
Slope as a % for conn. to a standard riser is next to %Slp.Cn.@Rsr.. Slope of conn. normally ranges from 1% to 10%. Slopes greater than 10% may be used only if
the velocity does not exceed 15 fps. If the velocity exceeds 15 fps the invert at the property line must be lowered. A negative slope means the invert at the property line
must be raised. Slopes of less than 1% may only be used if the velocity is at least 3 fps.
Enter the diameter of the conn. in inches under Dia.Cn./(in.) next to the appropriate conn. pipe material only. Rate of flow in cfs and velocity in fps at full flow is
shown for a conn. to a circular/brick egg sewer at 75% and 92% dia., (1 to 2 oclock), to a box/flat top circular bottom reinforced concrete section sewer, and to a riser.
Information for each conn. must be entered seperately and is computed individually.
For a conn. at an existing or proposed manhole enter the following in the appropriate datum above: invert of the sewer at the manhole next to Upstm.Mh.Inv.; sewer
diameter/height in inches or height in ft. as appropriate; distance in ft. from property line to sewer connecting to next to Dst.P.L.-Swr.(ft.); invert of conn. at property
line next to Inv.Cn.@P.L.; diameter of conn. in inches next to Dia.Cn.Mh.-in. and also under Dia.Cn./ (in.) next to the appropriate conn. pipe material. Maximum
and minimum inverts and slopes are shown for a conn. to a circular/brick egg sewer and to a box/flat top circular bottom reinforced concrete section sewer.
Slope of a conn. normally ranges from 1% to 10%. A slope greater than 10% may be used only if the velocity does not exceed 15 fps. If the velocity exceeds 15 fps
the invert at the property line must be lowered. A negative slope means the invert at the property line must be raised. Slopes of less than 1% may only be used if the
velocity is at least 3 fps.